## Slide 1
Armstrong Fluid Technology | 2014
Training April 2015
BSS – Controls and Optimization Systems
Controls offering
overview & E*P
IPS4000, and
IPC9500
Plant optimization
with IPC 11550 &
OPTI-VISOR

## Slide 2: Armstrong Design Envelope Plant Optimization
Armstrong Design Envelope Chiller Plant Optimization
Click the link below to view the Optimization Video:

## Slide 3
Plant Controls Overview
Plant Automation
IPC
Integrated Plant Control
IPC9500
Pump Station Controller
IPS
Integrated Pumping System Controller
IPS 4000
IPS 4500
All Variable Plant Optimization
IPC 11550
OPTI-VISOR
Controls Services;
Diagnostics, field service, Energy Analysis,
Audits
ECO*PULSE,
Factory Service Plan

## Slide 4
Plant Controls Overview
IPC9500
IPS 4000/4500
IPC 11550
OPTI-VISOR
ECO*PULSE,
Factory Service Plan

## Slide 5
Integrated Pump System Controller
IPS 4000
IPC9500
IPS 4000/4500
IPC 11550
OPTI-VISOR
ECO*PULSE,
Factory Service Plan

## Slide 6: IPS Background
Variable Flow
Pump Energy Savings
PID Feedback Control for sensors setting: dP, or return Temp
Variable Speed Control
Complementary to BAS
Sensorless feedback and parallel sensorless pump staging

## Slide 7: IPS – How does it work? Traditional speed control
COMFORT & ENERGY SAVINGS through pump speed control and equipment sequencing in a variable flow system.
IPS controls to the least satisfied zone, active zone.
Factory programmed algorithm, enables easy site configuration with field adjustable parameters.
Zone sensor settings are maintained by modulating pump speed and staging pump units.

## Slide 8: IPS 4000 – Parallel Sensorless Control Unit
  An upgrade to the prior IPS control systems, more streamlined, that covers range of the IPS3000 and IPS5000
  Enhanced control solution for Secondary pumping system.
  2. Touch screen display
  3. Multi Parallel pumping with Sensorless technology
  4. Valve control capability for campus loop ETS
  5. Multi language capability on the entire IPS offering
Notes: Designed with the industry's latest on variable speed pumping technology, the IPS4000 brings to us breakthrough solutions that enables variable speed pumping system exceeds the efficiency levels demanded by the market today. It leverages advance pumping control technology, offering flexibility yet simple to implement with the lowest installed and lowest operating cost.
The IPS4000 series controllers are specifically designed to control multiple secondary pumps for HVAC systems in both heating and cooling applications. The IPS4000 Controller is capable of controlling up to six (6) variable speed pumps in parallel or standby configurations and up to 12 zones.
The IPS 4000 series controller comes in the following configurations and ranges.
IPS 4001 (3 pumps and 2 zones)
IPS 4002 (4 pumps and 5 zones)
IPS 4003 (6 pumps and 12 zones

## Slide 10: IPS4000 Speed control options
Remote dP zone sensor
Return Temperature sensor
Sensorless control curve
PSPC technology
Campus Loop ETS valve control

## Slide 11: IPS4000 – Temperature Sensing & Valve Control Capability (energy transfer station for tall building)
A PID loop logic with an input (the Temperature) and an Output (the signal to open or close the valve).
Scenario 1
When the building is high and needs a 2nd loop with sets of pumps on top of a 1st loop (to reach the top of the building), then the Temperature sensor T1 sends a signal through the PID to open the valve of the 1st loop to get more cooling exchange

## Slide 12: IPS4000 – Temperature Sensing & Valve Control Capability (energy transfer station on campus loop)
A PID loop logic with an input (the Temperature) and an Output (the signal to open or close the valve).
Scenario 2
When the supply & return are connected to a main supply & return (when the building is part of a larger campus for example), then the Temperature sensor T1 sends a signal though the PID to open the 3-way valve to bypass the flow when the water is cold enough and does not need to go back to the main supply & Return.

## Slide 13
IPS4000 – Has its own internal sensorless control sequence, and PSPC technology (on the IPS400)

## Slide 14: Design Envelope Parallel Sensorless
Mimics the performance of a sensor by pre-programming pump curve characteristics into the integrated controls
IPS 4000 Control Unit

## Slide 15: IPS4000 with DE Pumps Wall space savings
No room on wall for multiple VFDs
Notes: IPS with an IVS DE Pump require less space, where the IPS can be located on a much preferred area versus with it comes as a rack assembly.

## Slide 16: Integrated Pump Systems Sensorless Speed Control with IPS4000
Simple on screen setup to adjust as built design flow and head parameters
Parallel Sensorless Pump Control staging points automatically recalculated for the as built entered condition (no modifications at the pump)

## Slide 17: Sensorless Set up
IPS4000 can operate up to 6 pumps in Sensorless
Reads Head and Flow on each pump
Read Current, power, and speed feedback.
Flow, Head BEP (Best Efficiency Point) Set up
Unit of measure set up
Dead Band set up (avoid constant staging)
Notes: This screen is only available when the VFD type is IVS sensorless, it complements the pump overview screen. If there are more than 3 pumps, scroll using the arrows on the top corners.
The pump speed and best efficiency staging points are controlled by embedded Armstrong algorithm to maintain the operation point (system head & flow) on the system control curve.
The control monitors the flow of each running pump and if it deviates more than 20% off the average the system will issue an alarm.
If the pump dp switches are enabled, the ips will use their signals (di) as pump operation confirmation. If the dp switches are not enabled, the vfd feedback is used as pump run confirmation.

## Slide 18
Notes: temperature control of modulating valve
If the temperature control is enabled, the ips 4000 will use one of the zone sensor analog inputs for a temperature sensor, and pump four analog output to control the modulating valve.
The valve position is controlled by pid to maintain the temperature at a setpoint specified by the user.
The valve output is selectable between 0-10 VDC or 2-10 VDC.

## Slide 19: Communications Set up Get IPS4000 BACnet serial addresses from Tech Support
Notes: temperature control of modulating valve
If the temperature control is enabled, the ips 4000 will use one of the zone sensor analog inputs for a temperature sensor, and pump four analog output to control the modulating valve.
The valve position is controlled by pid to maintain the temperature at a setpoint specified by the user.
The valve output is selectable between 0-10 VDC or 2-10 VDC.

## Slide 20: Temperature return speed control situation Converting 3-Way Valve Constant Flow Systems
An Easier Implementation
IPS4500 pump control can adjust based on return temperature zones to regulate pump speed.
Pumps can be made variable flow based on return temperature signal
Flow and system dP received from Design Envelope pumps
NOC received from BMS

## Slide 21: Integrated Pump System 4000 Compliments DE Pumps
Armstrong sensorless pump control can be enabled on the IPS 4000 with additional zone sensors, for buildings with critical zones
IPS4000 controller can apply parallel sensorless pump control, for more than 4 pumps or use up to 12 zone sensors for pump control
1
2
3

## Slide 22: IPS4000 – Value Proposition
  IPS controllers provide great energy savings, prolong equipment life, while still maintaining occupant comfort
  IPS controllers come with a large number of native communications protocols that are standard in the HVAC industry (reducing the need of expensive gateways)
  Risk minimization, since pumping controls are from one supplier, especially an HVAC equipment supplier
  IPS controllers are catalogued product, (this keeps things simple i.e.: submittals, replacement parts, service)
  Pre-engineered makes this a reliable, proven solution at a economic price level
  Sensorless technology on parallel pumping control can be used to reduce capital cost on sensors and installation
Notes: Parallel Sensorlesss Technology with Design Envelope Pumps
Multi zone feedback control
Enhanced Control Capabilities and performance data for Optimized Staging of pumps
Easy selection as a pre-engineered catalogue offering
Support for full serial communication using industry standard protocols
Integration with a new or existing HVAC system, operating either in a standalone mode, or through the building automation system

## Slide 23: Where to use IPS4000 Solutions
IPS solutions can be used:
To optimize the control of any traditional pumping system with any variable speed drives.
Variable speed pumps save energy, but the level of savings depend on the control strategy.
Where multi-zone control is required even greater energy savings and closer comfort can be achieved.
Sensor less technology with DE pump on parallel pumping control can be used to reduce capital cost and optimized control.
To optimize the control of Armstrong Design Envelope pumps, saving site space and maximizing energy savings
Notes: 23

## Slide 24: AOL Documents
Submittal reports
BAAN order entry reports
Wiring Diagram
Terminal Block Diagram
Specification report

## Slide 25: IPS 4000 Supporting Documents
Product Brochure
Detailed Specification
Installation and Operating Guide
Sequence of Operation

## Slide 26
IPS 4000 Competitive Distinction (Cheat sheet) soon available!

## Slide 27: QA Session

## Slide 28
Plant Automation Controls Overview
IPC9500
IPS 4000
IPC 11550
OPTI-VISOR
ECO*PULSE,
Factory Service Plan

## Slide 29
Intelligent Plant Control
IPC 9511 Air cooled Chiller Plant Automation
IPC 9521 Water cooled Chiller Plant Automation
Notes: Continually growing on our controls portfolio, we at Armstrong are pleased to announce the launch of our latest addition to our control offering with our new IPC 9511 series.
29

## Slide 30
IPC 9511
Air Cooled Plants
Variable Primary
Optimizes Plant for chiller and pump configurations
IPC 9521
Water Cooled Plants
All Variable
Optimization of plant for tower, chiller and pump configurations
IPC9500 – Integrated Plant Control Value
Robust factory built automation system for variable speed chilled water plant controls
Catalogue product
Site configurable
Stand-alone or complementary with BAS
Remote access for support/troubleshooting
Notes: We have developed a series of control and product solutions that revolve around integrated control, one family of these is our line of all variable speed chilled water plant controls.
These are robust factory built automation systems specific for a variety of chiller plant configurations, include all-variable speed plants: chillers, tower fans, CW pumps, and chilled water pumps.
These are site configurable devices, during commissioning the installer is inputting process data such as number of chillers and capacity of chillers, as opposed to creating any site specific operating code.
Important for your business is that they network with building automation systems, and enable remote access for your support of the customer relationship.

## Slide 31: IPC 9511/21 Overview Air/Water Cooled Chiller Plant Automation
  Basic Features
  Automates all-variable chiller plants
  Standard Product solution for up to 5 chillers / 5 primary pumps + 5 condenser pumps / 5 cooling towers
  Includes ability to sequence chiller isolation valves and system by-pass valve in the de-coupler
  Compliance with 90.1 for low load pump speed set-point set-back
  Chilled water supply temperature reset
  Data storage and remote access with secure connection

## Slide 32: IPC 9500 – Intuitive interface
Multicolor Plant overview with an Active schematic of the hydronic system indicating:
  Plant configuration (adjustable)
  Operating status of each equipment
  On-screen help functions for each parameter.
Simple to Operate and Commission through the 10” touchscreen OR through a web browser locally or remotely.
Notes: Simplicity of the implementation is achieved with an intuitive interface.
The screen gives a Multicolor Plant overview with an active schematic of the system picked among several standard chiller configurations already preprogrammed. During commissioning the installer is inputting process data such as number of chillers and capacity of chillers, number of pumps, if they are headered or dedicated, chiler points list…etc
The screen view updates automatically to reflect changes in the plant configuration.
During the operation, the screen view also updates to indicate the operating status of each equipment (operating, stopped or in alarm)
On-screen help functions for each parameter also guide the installer during the commissioning.
So with this intuitive screen it really simplifies the commissioning and the operation. The interface can also be accessed through a web browser locally or remotely as needed.

## Slide 33: IPC 9511- Standard Features
Site adjustable
Notes: And important to mention: those quantities and configuration can be adjusted on site with no hardware or program change.

## Slide 34: IPC 9521- Standard Features
Site adjustable
Enclosure Options:
Nema 12 (Indoor)
Nema 4X (Outdoor)
Notes: And important to mention: those quantities and configuration can be adjusted on site with no hardware or program change.

## Slide 35: Application with DE Pumps Variable Primary with Sensorless Speed Control
Coordination of pump speed for staging of chillers and by-pass flow valve
Plant controller IPC9511 (air cooled) and IPC9521(water cooled) have sensorless control curves and patent pending PSPC

## Slide 36: Integrated Pump Systems Variable Primary with Sensorless Speed Control
Coordination of pump speed for staging of chillers and by-pass flow valve
Plant controller IPC9511 (air cooled) and IPC9521(water cooled) have sensorless control curves and patent pending PSPC

## Slide 37: IPC 9500 Overview Water Cooled Chiller Plant Automation
  Our UNIQUE capabilities :
  Optimizes staging of primary pumps for true best efficiency
  Quadratic control curve for optimized system delta T, and plant efficiency with comfort
  Can convert 3-way valve distribution systems to variable flow
  Remote device serial communications configurable from the setup screen
  Available as basic 90.1-2013 compliant configuration, and owner can upgrade to higher optimization modules at future date
Notes: The IPC9521 provides a full automation as a BMS would provide but with additional optimization features and options that the plant module of a BMS can’t match.
If associated with Design Envelope pumps on the primary loop, the true best efficiency staging optimization can be therefore applied. In tandem with Design Envelope pumps, Parallel SensorlessTM staging of pumps can be implemented to meet system demand while maintaining minimum flow rates for the chillers in operation.
As well as the true best efficiency, the IPC9521 will empower the quadratic control curve to respond to system demand for an optimized system delta T and an improved plant efficiency, increasing the building comfort.
The IPC9521 is a great opportunity to convert a 3-way valve distribution systems to a variable flow system.
Several standard chiller configurations are already preprogrammed. The screen view updates automatically, reflecting changes in the plant configuration. Identically, remote device serial communications are configurable from the setup screen. With further parameters also configurable directly on screen, it makes this control system the first one type in its category.
Finally, as mentioned previously, the IPC 9521 is available as basic 90.1 compliant configuration. Nevertheless if building condition and requirement change with time, the owner will be able to upgrade to higher optimization modules at future date.

## Slide 38: IPC 9500 – Meeting ASHRAE Standards
Complies with ASHRAE 90.1-2013 including enhanced embedded control features using:
    Cooling valves optimization (6.5.4.2):
      Receives a signal from the BAS of the most open cooling valve.
      Regulates the pumps speed to maintain the position as open as possible.
      Saves energy by reducing system pressure loss
    Hydronic variable flow systems (6.5.4.2):
      provides 70% savings when system flow is at 50% of design.
Notes: Compliance with ASHRAE 90.1 2013
- provides 70% savings when system flow is at 50% of design
  - As flow/load decreases, the controller reduces the pump speed and keeps one valve as open as possible.
6.5.4.2 Hydronic Variable Flow Systems. HV AC pumping systems having a total pump system
power exceeding lO HP that include control valves designed to modulate or step open and close as
a function of load shall be designed for variable fluid flow and shall be capable of reducing
pump flow rates to 50% or less of the design flow rate. Individual chilled-water pumps serving
variable-flow systems having motors exceeding 5 hp shall have controls and/or devices (such as
variable-speed control) that will result in pump motor demand of no more than 30% of design
wattage at 50% of design water flow. The controls or devices shall be controlled as a function of
desired flow or to maintain a minimum required differential pressure. Differential pressure shall be
measured at or near the most remote heat exchanger or the heat exchanger requiring the greatest
differential pressure. The differential pressure setpoint shall be no more than 110% of that required
to achieve design flow through the heat exchanger. Where differential pressure control is used to
comply with this section and DOC systems are used, the setpoint shall be reset downward based on
valve positions until one valve is nearly wide open.

## Slide 39: IPC 9500 – Minimizing points list
Available preprogrammed point lists pending on the chiller brand and the communication protocol :
Reduce the commissioning time.
Remove complexity and reduce risk of the project
Notes: One of the key parameters I just mentioned which can also be selected form the touchscreen, is the chiller point list already preloaded.
Pending on the Chiller make and the communication protocol between the IPC9521 and the installed chillers, the installer can directly select the most recent point list from York, McQay, Trane or Smardt.
Not only the programing, which usually happens during the commissioning, is not necessary anymore, for those chiller makes, but the adjustments which usually happen to coordinate the data (such as chiller kW, chilled water supply temperature….) therefore the communication points between the control system and the chiller are already aligned.
This is a neat and key function, that no other control system has.
Combined to the other key attributes, it will definitely remove complexity and reduce risk of the project during the commissioning.

## Slide 40: Product Range – Efficiency comparison, NYC (oil lubricated VS chillers)
Chart: IPC Energy Savings Expectations 1500 TONS - New York
| Base Case | IPC 9521 | IPC 9541 | OPTI-VISOR w/. BMS | IPC 9551
 | 0.89 | 0.71 | 0.67 | 0.62 | 0.59
IPC 9521
+ CW
optimization
IPC9521
With
OPT-VISOR
 | Notes & Assumptions | 
 | 3 x 500 Ton VS Centrifugal Chillers | 
 | Base Case Configuration: | IPC Case Configurations:
Primary pumps | Constant Primary | Variable Primary
Chillers | Typical VS Centrifugal | Typical VS Centrifugal
Condenser Pumps | Constant Speed | Variable Speed
Cooling Tower Fans | Variable Speed | Variable Speed
Notes: The following simple case study is to indicate how the IPC9521 will perform by comparing few different configurations and level of optimization.
For that simple case study, we took an installation using the New York climate and its outside air temperature. We considered 3 identical chillers (500 TONS each, oil lubricated Variable Speed Chillers) for all the cases.
For reference we took a standard base case configuration with Constant Primary pumps. For that climate and configuration, it would perform at about 0.89 kW/Ton.
The automation and the base optimization with the 9521, installed to run as a variable primary system, will allow to drop the plant efficiency to 0.71 kW/TON.
The first optimization upgrade package you will be able to upload and which is the Condenser loop optimization, will drop a bit more the efficiency to 0.67 kW.
On an other hand if you choose to upgrade the package by combining an IPC9521 with Opti-Visor, it will bring to an even better plant efficiency with 0.59 kW/TON.
Just for reference (in red), the identical installation with an OPTI-VISOR and the BMS for automation would give 0.62kW/TON.

## Slide 41: IPC 9500 – Who and How to Sell
  Consultant
  Owner Promotion
  Contractor Leveraging
  OEMs

## Slide 42: IPC 9500 – How to Sell New Construction / Consultants
  Consultant (Energy or New Construction/ Existing Building)
    Specification selling
    For small and medium projects, where there is a simple BMS or no BMS
    For LEED and or 189.1 compliance
    In the controls section of the specification
    Synergy optimized with Design Envelope pump, best value even without the Armstrong pumps

## Slide 43: IPC 9500 – How to Sell Owners
  Owners (Energy or New Construction/ Existing Building)
    Simplicity of operation
    Reduced dependency for the operators to operate through the BMS
    Fully compatible and complimentary to the BMS
    Easy to upgrade an existing system for automation where none existed
    Many future options for optimization and diagnostics that other system do not offer
    Ideal for integration with a Design Envelope pump installation – get more value, performance, and functionality than with the BMS or the Design Envelope pumps alone

## Slide 44: IPC 9500 – How to Sell Contractors
  Contractors (Energy or New Construction/ Existing Building)
    Simplicity of implementation
    Flexibility for on site configuration
    Can have the plant commissioned well before the rest of the building and set in AUTO
    Keeps the scope of the plant with the “plant team” as opposed to dependency on tie-ing in with the bigger controls scope
    Factory tested reliability
    Lower over-all project cost
    Optimized thermo-dynamic performance for overall plant performance
    Separate user interface for the mechanical team to gather data and do remote post install assessments

## Slide 45: IPC 9500 – How to Sell OEMs
  OEMs (Chiller Manufacturer, Packagers)
    Allows total control implementation of larger air cooled systems without engaging the BMS for execution
    Keeps the operating parameters for a variable primary solution in their control for protection of the chillers and minimize call-backs
    Is something that their technicians and service teams can look into remotely for detailed answers about what is happening at the site (this can be tough to find / access with BMS site solutions, or slow to receive)
    A complementary product, that increases their share of the pie
    Leverages their position to also include Design Envelope pumps to get the synergy of IPC with the Armstrong pump solution (even greater added value)

## Slide 46
IPC 9500 Controls Offerings
Data Centers
Integrated Plant Control Systems
IPC9511 Air Cooled
IPC9521 Water Cooled
Both Control systems will be available with a Tier III and IV data center compliant scheme for n+1
The configuration will provide “hot-swap” of automation functionality with a “mirror” operating scheme.
Notes: 46

## Slide 47: VPF Application Matrix – Armstrong Has You Covered!

## Slide 48
IPS 9500 Competitive Distinction (Cheat sheet) soon available!

## Slide 49: IPC 9500 Supporting Documents
Technical overview
Detailed Specification
Installation and Operating Guide
Submittal
Product Brochure
Sequence of Operation

## Slide 50: AOL Selection –available – IPC 9500 Chiller plant automation (IPC)

## Slide 51: AOL Documents
Submittal and Specification reports
Field Wiring and Terminal Block Diagrams

## Slide 52: Design Envelope IPC 9500 Our Key Differentiators
  Sensorless and Parallel Sensorless (PSPC) technology for VARIABLE PRIMARY SYSTEMS
  Optional Optimization Packages, future upgrades:
      Condenser loop optimization
      Integration with an OPTI-VISOR
      ECO*PULSE Health Service & Diagnostics
  On screen configuration of serial communication to controlled equipment, and to external (BMS) devices, with Prelisted Modbus/BACnet/Lonworks mapping for different chiller makes
  Programming flexibility: ability for controls contractors to customize/add to additional logic to the existing Armstrong factory control logic
Notes:   Sensorless and Parallel Sensorless technology for VARIABLE PRIMARY SYSTEMS saves money :
    no dP sensor
    increased efficiency vs capacity staging of pumps (Optimizes staging of pumps for true best efficiency & Quadratic control curve for optimized system delta T, and plant efficiency with comfort)
  Available as basic 90.1 compliant configuration, and owner can upgrade to higher optimization modules at future date, future upgrades :
  Easy Performance Upgrade after construction :
  Low price on bid day
  Plug and play optimization
  Future changes to plant (# of chillers, pump types, etc) can be implemented through the touchscreen – without programming/testing requirements.
  Remote device serial communications configurable from the setup screen.
        Pre-configured, listed Modbus/BACnet/Lonworks mapping for several chillers;
        Factory tested for minimal troubleshooting;
        Intuitive menu item selection for ease of setup

## Slide 53: Design Envelope 9500 Value Proposition
  A price competitive plant automation solution for small and medium plant sizes, GETS CONTRACTOR ATTENTION
  Ease of use, remotely serviced, troubleshoot, modify and download the IPC software (hot swap).
  Occupant comfort through multi-leveled redundant logic to ensures operation even after sensor failures
  Optional optimization upgrade feature to sell to “owner” for greater energy savings,
  Lowest installation cost as communications and equipment points list are pre-configured – an INDUSTRY FIRST
  Lower cost
  Risk reduction
  Risk reduction
  Energy Savings
  Lower cost
Notes:   So in summary, the IPC 9521 provides a value proposition by :
  ….
  Already available for the North and South America as well as for the India & ME markets. and currently being implanted in other regions.

## Slide 54
IPS 9521 Remote Demo Site
Remote Demonstration site - IPC 9521
User = “sim”, keep Password blank

## Slide 55
Plant Optimization Controls Overview
IPC9500
IPS 4000
IPC 11550
OPTI-VISOR
ECO*PULSE,
Factory Service Plan

## Slide 56
Design Envelope Integrated Plant Control
IPC 11550
A BUSINESS SOLUTION
That Delivers:
Up to 60% life cycle cost savings
Notes: A long list of savings that adds up to a LCC and a true value based offering.

## Slide 57
.90
.75
.55
10-20 years
6-10 years
0-5 years
Design Envelope IPC
Chiller plant age
1.1
Total plant kW/ton
25-50%
Design Envelope Integrated Plant Control (IPC)
50% savings over standard traditional plant
Plant Optimization with
Integrated Plant Control
Notes: 57
57

## Slide 58
Tower or Chiller Retrofits
Additional Capacity Requirements
Refrigerant Change Outs
Utility Rebates ($0.05/kW-hr)
> 3,000,000 ton hours (2000tons at 3000 hours)
The “no-brainer” situations to watch for
They bring you <1 year payback on plant upgrade
OR
Regular
6 – 24 month paybacks
Notes: 58

## Slide 59
Key differences to Armstrong
Design Envelope Integrated Plant Control
Digital control algorithms that work from computer base equipment performance maps (not feedback control)
The ability to effectively operate the cooling tower in a variable water flow mode (not just fan speed)
Mechanical Equipment Manufacturer built and tested controller platform, fully interoperable with the BMS (not an island)
15%
10%
15%
40%
Notes: 59

## Slide 60
Reduced Water Consumption
Design Envelope Integrated Plant Control
All of the electrical power drawn from the plant equipment manifests itself primarily as heat in the cooling system
To remove that heat from the equipment, the cooling tower evaporative process consumes water
By drawing less electrical power with Integrated Plant Control, less heat needs to be rejected by the cooling tower
Less heat rejected at the tower means less water consumption at the tower
40%
4-12%
Notes: 60

## Slide 61
Plant Annual energy Savings of 30-60%
Design Envelope Integrated Plant Control
The Benefits of Optimization
Annual Water Savings on the Cooling Tower of 4-12%
Longer Plant Equipment Life, 20-30%
Protect your ROI with ECO*PULSE On-board Diagnostic Service saving 5-20% annual energy costs
kW-hr
30-60%
$
H2O
4-12%
$
Life
20-30%
$
ROI
5-20%
$
Notes: 61

## Slide 62
Existing practice (CPVS)
Analog era
Feedback loop (PID)
Silo sub-system control
VS chillers, variable secondary CW reset
0.76 kW/ton (COP 4.7)
0.78 kW/ton (COP 4.6)
0.72 kW/ton (COP 4.9)
Existing best in class
Analog era
Feedback loop (PID)
Silo sub-system control
Variable primary flow (VPF) with CHW & CW reset
0.72 kW/ton (COP 4.9)
0.75 kW/ton (COP 4.7)
0.68 kW/ton (COP 5.2)
Design Envelope integrated demand based
Digital era
Demand based relational
Integrated plant solution
All-variable chiller plant
0.50 kW/ton (COP 7.1)
0.56 kW/ton (COP 6.3)
0.48 kW/ton (COP 7.4)
Moderate
Humid
Arid
Plant efficiency
New Variable Speed Chiller Plants
>.76 kW/ton
>.72 kW/ton
<.50 kW/ton
Armstrong’s Chiller Plant Optimization
Notes: 62

## Slide 63
Existing practice (CPVS)
Analog era
Feedback loop (PID)
0.76 kW/ton (COP 4.7)
Existing best in class
Analog era
Feedback loop (PID)
0.72 kW/ton (COP 4.9)
Design Envelope integrated demand based
Digital era
Demand based relational
0.50 kW/ton (COP 7.1)
Moderate
Plant efficiency
New Variable Speed Chiller Plants
Armstrong’s Chiller Plant Optimization
Notes: 63

## Slide 64: Traditional chiller plant control process set-point based
BMS
Capacity based sequencing
Automation Sequence
Parallel equipment staging (up/down)
Equipment speed control
Silo sub-system control
PID feedback control loops
Ambient reset
Traditional
Logic
Notes: What if the BMS did not look a the system as items of equipment that it enables and controls to a given set of pre-determined instructions. What if it viewed the system as a whole and understood the power relationships, physcometry and linked all this into the actual needs of the building.
What if it based the sequencing and operating point of the equipment based on the actual needs of the building demand (we d this on the secondary side with DP control etc, but generally do not use this same theory on the primary plant control). Rather than a set point temperature.
What if we actually looked at the performance curves for the equipment within the system and moulded these together to offer a overall increased performance.
If you need an analogy discuss racing cars (tyres, suspension, aerodynamics etc) or a cycling peloton

## Slide 65: Conventional PID Feedback Loop Control Limitations
Challenges:
Multiple reset points
Part Load Comfort
Hunting
Silo operation not plant efficiency
PID FB LOOP
PID FB LOOP
PID FB LOOP

## Slide 66: Patented Armstrong Design Envelope Integrated Plant Control
Performance Curve Based
Heat Transfer and Power Consumed
demand with power relationships
View Equipment As Performance Maps: Tons of cooling (kWc), and Electrical Power
IPC
Notes: What if the BMS did not look a the system as items of equipment that it enables and controls to a given set of pre-determined instructions. What if it viewed the system as a whole and understood the power relationships, physcometry and linked all this into the actual needs of the building.
What if it based the sequencing and operating point of the equipment based on the actual needs of the building demand (we d this on the secondary side with DP control etc, but generally do not use this same theory on the primary plant control). Rather than a set point temperature.
What if we actually looked at the performance curves for the equipment within the system and moulded these together to offer a overall increased performance.
If you need an analogy discuss racing cars (tyres, suspension, aerodynamics etc) or a cycling peloton

## Slide 67
BMS
IPC
Two different system control philosophies
Component based
System based
Notes: What if the BMS did not look a the system as items of equipment that it enables and controls to a given set of pre-determined instructions. What if it viewed the system as a whole and understood the power relationships, physcometry and linked all this into the actual needs of the building.
What if it based the sequencing and operating point of the equipment based on the actual needs of the building demand (we d this on the secondary side with DP control etc, but generally do not use this same theory on the primary plant control). Rather than a set point temperature.
What if we actually looked at the performance curves for the equipment within the system and moulded these together to offer a overall increased performance.
If you need an analogy discuss racing cars (tyres, suspension, aerodynamics etc) or a cycling peloton

## Slide 68
Patented Optimization Control
(based on Hartman LOOP)
Armstrong holds an exclusive license for FACTORY Implementation of Hartman LOOP Technology.
Optimum Energy has acquired the Patents from Mr. Hartman, yet honors the license agreement with Armstrong
Notes: This brings us to the first element of our control methodology, “natural curve”. The natural curve is defined as the line that joins the best efficiency point for each of multiple scenarios, in this case the scenarios are 4 different entering condenser water temperatures.
Natural curve sequencing says that parallel equipment, in this case parallel chillers, should be sequenced such that they operate a close a possible to the natural curve.
So, if we had a plant with 3 parallel variable speed chillers and the plant was operating at 33% load with 19C entering condenser water, and we sequenced the chillers using traditional capacity based sequencing we would be operating one chiller, on the blue line at 100%, which would be a chiller efficiency of 0.4 kW/ton. If we applied natural curve sequencing we would operate 3 chillers at 33% each, for a chiller efficiency of 0.3 kW/ton, with a net efficiency gain on the chillers of 25%, just be using a different sequencing methodology on the same mechanical equipment.
I can’t stress how much this goes against tradition. The main point being that mechanical operators have always thought to minimize the number of pieces of plant equipment operating because they are thought to be more efficient at full load, and starting other equipment would prematurely wear the plant down.
For part load applications, we move from the top right to the bottom left.

## Slide 69
Patented Optimization Control
(based on Hartman LOOP)
The patents are a “method” to optimize chiller plant efficiency by implement sequences that execute to certain rules as outlined in the claims of the 3 patents.
Armstrong’s 4 core competencies have been extremely valuable in devising an implementation of those rules to arrive at a more stable, robust and efficient set of control algorithms leading to better overall performance of the plant; heat transfer, fluid flow, variable speed and demand based control.
Notes: This brings us to the first element of our control methodology, “natural curve”. The natural curve is defined as the line that joins the best efficiency point for each of multiple scenarios, in this case the scenarios are 4 different entering condenser water temperatures.
Natural curve sequencing says that parallel equipment, in this case parallel chillers, should be sequenced such that they operate a close a possible to the natural curve.
So, if we had a plant with 3 parallel variable speed chillers and the plant was operating at 33% load with 19C entering condenser water, and we sequenced the chillers using traditional capacity based sequencing we would be operating one chiller, on the blue line at 100%, which would be a chiller efficiency of 0.4 kW/ton. If we applied natural curve sequencing we would operate 3 chillers at 33% each, for a chiller efficiency of 0.3 kW/ton, with a net efficiency gain on the chillers of 25%, just be using a different sequencing methodology on the same mechanical equipment.
I can’t stress how much this goes against tradition. The main point being that mechanical operators have always thought to minimize the number of pieces of plant equipment operating because they are thought to be more efficient at full load, and starting other equipment would prematurely wear the plant down.
For part load applications, we move from the top right to the bottom left.

## Slide 70
Patented Optimization Control
(based on Hartman LOOP)
Armstrong’s 4 core competencies; heat transfer, fluid flow, variable speed and demand based control.
This differentiates us in our results on plant optimization initiatives, compared to controls companies who do not have the in depth mechanical equipment design, manufacturing, and operating experience.
Notes: This brings us to the first element of our control methodology, “natural curve”. The natural curve is defined as the line that joins the best efficiency point for each of multiple scenarios, in this case the scenarios are 4 different entering condenser water temperatures.
Natural curve sequencing says that parallel equipment, in this case parallel chillers, should be sequenced such that they operate a close a possible to the natural curve.
So, if we had a plant with 3 parallel variable speed chillers and the plant was operating at 33% load with 19C entering condenser water, and we sequenced the chillers using traditional capacity based sequencing we would be operating one chiller, on the blue line at 100%, which would be a chiller efficiency of 0.4 kW/ton. If we applied natural curve sequencing we would operate 3 chillers at 33% each, for a chiller efficiency of 0.3 kW/ton, with a net efficiency gain on the chillers of 25%, just be using a different sequencing methodology on the same mechanical equipment.
I can’t stress how much this goes against tradition. The main point being that mechanical operators have always thought to minimize the number of pieces of plant equipment operating because they are thought to be more efficient at full load, and starting other equipment would prematurely wear the plant down.
For part load applications, we move from the top right to the bottom left.

## Slide 71
Patented Optimization Control
(based on Hartman LOOP)
Armstrong Optimization based around Patented Sequences;
Natural curve sequencings
Equal marginal performance principle
Demand Based Control
Notes: This brings us to the first element of our control methodology, “natural curve”. The natural curve is defined as the line that joins the best efficiency point for each of multiple scenarios, in this case the scenarios are 4 different entering condenser water temperatures.
Natural curve sequencing says that parallel equipment, in this case parallel chillers, should be sequenced such that they operate a close a possible to the natural curve.
So, if we had a plant with 3 parallel variable speed chillers and the plant was operating at 33% load with 19C entering condenser water, and we sequenced the chillers using traditional capacity based sequencing we would be operating one chiller, on the blue line at 100%, which would be a chiller efficiency of 0.4 kW/ton. If we applied natural curve sequencing we would operate 3 chillers at 33% each, for a chiller efficiency of 0.3 kW/ton, with a net efficiency gain on the chillers of 25%, just be using a different sequencing methodology on the same mechanical equipment.
I can’t stress how much this goes against tradition. The main point being that mechanical operators have always thought to minimize the number of pieces of plant equipment operating because they are thought to be more efficient at full load, and starting other equipment would prematurely wear the plant down.
For part load applications, we move from the top right to the bottom left.

## Slide 72
Patented Control (based on Hartman LOOP) Natural curve sequencing vs traditional capacity based
Chart: Natural Curve Sequencing
| 0.05 | 0.1 | 0.15000000000000019 | 0.2 | 0.25 | 0.30000000000000032 | 0.35000000000000031 | 0.4 | 0.45 | 0.5 | 0.55000000000000004 | 0.60000000000000064 | 0.65000000000000102 | 0.70000000000000062 | 0.75000000000000089 | 0.8 | 0.85000000000000064 | 0.9 | 0.95000000000000062 | 1
VS ECWT 13°C | 6.625 | 7.2661 | 8.1909 | 9.3854 | 10.4768 | 11.2625 | 12.2752 | 12.8715 | 13.25 | 13.25 | 12.8715 | 12.5139 | 12.1757 | 11.8553 | 11.5513 | 10.9878 | 10.7262 | 10.2387 | 10.0111 | 9.5851
VS ECWT 18°C | 5.6241 | 6.1432 | 6.7679 | 7.5341 | 8.4959 | 9.2862 | 9.9827 | 10.265 | 10.3716 | 10.3716 | 10.2387 | 10.1091 | 9.787 | 9.5073 | 9.0752 | 8.776 | 8.5873 | 8.3189 | 7.9862 | 7.679
VS ECWT 24°C | 4.9843 | 5.4177 | 5.9337 | 6.4452 | 7.1888 | 7.7879 | 8.3071 | 8.4005 | 8.5936 | 8.4959 | 8.4959 | 8.4005 | 8.2158 | 7.9536 | 7.629 | 7.3732 | 7.1204 | 6.8591 | 6.6754 | 6.5496
VS ECWT 29°C | 4.3924 | 4.6852 | 5.0199 | 5.4905 | 6.0585 | 6.63 | 6.89 | 7.0278 | 7.0278 | 6.89 | 6.7575 | 6.63 | 6.5072 | 6.3889 | 6.2748 | 6.1963 | 6.0428 | 6.0067 | 5.8565 | 5.77
55F
65F
75F
85F
Capacity
Based
IPC
Notes: This brings us to the first element of our control methodology, “natural curve”. The natural curve is defined as the line that joins the best efficiency point for each of multiple scenarios, in this case the scenarios are 4 different entering condenser water temperatures.
Natural curve sequencing says that parallel equipment, in this case parallel chillers, should be sequenced such that they operate a close a possible to the natural curve.
So, if we had a plant with 3 parallel variable speed chillers and the plant was operating at 33% load with 19C entering condenser water, and we sequenced the chillers using traditional capacity based sequencing we would be operating one chiller, on the blue line at 100%, which would be a chiller efficiency of 0.4 kW/ton. If we applied natural curve sequencing we would operate 3 chillers at 33% each, for a chiller efficiency of 0.3 kW/ton, with a net efficiency gain on the chillers of 25%, just be using a different sequencing methodology on the same mechanical equipment.
I can’t stress how much this goes against tradition. The main point being that mechanical operators have always thought to minimize the number of pieces of plant equipment operating because they are thought to be more efficient at full load, and starting other equipment would prematurely wear the plant down.
For part load applications, we move from the top right to the bottom left.

## Slide 73: Variable Speed Chiller (Power ~ Speed3 Relationship)
Three Ways To Achieve Speed Reduction of the Compressor; - Load Reduction
- Lower Entering Condenser Water
- Raise CHW Supply Temperature
Heat Load from Building
Heat Rejection from Chiller

## Slide 74
Natural curve sequencing vs traditional capacity based
Here – can the first chiller change from red to green from bottom to top up to about 75%. Then the second one changes up to about 40% and the first one drops to 40. they then both rise together to about 70% and the 3rd one rises to 40% and the first two drop to 40% - so they all end up at 40%.
At the same time the black circles follow the blue lines correspondingly.
Chiller 1 (lead) - 40%
Chiller 2 (lag 1) - 40%
Chiller 3 (lag 2) – 40%
Chiller 1
Chiller 2
Chiller 3
0%
100%
20%
40%
60%
80%
Notes: This sequence shows the chillers loading up based on natural curve principles such that the chillers spend as much time at or around the peak efficiency point as possible.
In this scenario, at 60% cooling load with all three chillers operating at 40% of capacity, very close to their peak efficiency, chiller COP will be above 11.0.
A 40% increase in chiller efficiency….!!!
The other thing we can do is to remember that our system has been designed on a 5 or 6 deg delta T, we can now start to slow down the primary chilled water (the kW cooling load remains the same) flow through the evaporators or even allow the chilled water leaving temperature to rise. Slowing the pumps down to match the load will run the compressors longer (or maybe even continually) but any increase in consumption through the compressor may be offset by the pumps.
Increasing the CHW set point would again reduce the load on our system (not as much de-suerheat) and have minimal effect on the overall system dynamics (i.e maintain the return temperature).

## Slide 75
Natural curve tower sequencing
approach temperature effects
Lower the leaving tower water temperature with:
Natural curve sequencing,
Variable flow towers, and
the same or less power
3
3
3
2
3
1
33%
66%
100%
Notes: Tower ETW Approach Temperature For 3 Tower Systems
Now lets take a bigger perspective and see the impact of natural curve sequencing on the “all variable speed” plant, not just the chiller as a stand alone device, and compare this to a traditional capacity based sequenced plant with constant flow cooling towers.
The chart displayed shows the approach temperature for a 3 chiller plant with a design wet bulb temperature of 77F at design day load. The approach temperature for the capacity sequenced constant flow cooling tower is shown by the read bar, and the approach temperature for the all variable speed plant with natural curve sequencing is shown by the grey bar. On design day the approach temperature for both plants is approaching 50F.
The approach temperature of the cooling tower is defined as the difference between the entering tower water temperature and the ambient wet bulb temperature. So on design day the entering tower water temperature is 95F water coming to the cooling tower from the chiller.
Now, on a 2/3rd load day the capacity sequenced plant will destage one chiller and destage one cooling tower. Operating with 2 chiller and 2 cooling towers at 100%, this configuration has the same sqft of tower surface area per kW load of cooling effect as was present on design day. The ambient temperature on the 2/3rd load day however will be cooler, and as the air temperature is cooler, it has less moisture capacity than the design day air temperature, and as a result the evaporative effect of the cooling tower is not as great as it was on design day and the approach temperature of the towers will go up.
With the all variable speed plant, and natural curve sequencing, we will keep all three cooling towers and chillers running, but just slow them down to meet the new load point. In this configuration we are leveraging the full cooling tower design day surface area, and keeping it all active for maximum evaporative effect at part flow. The result is that we are actually able to reduce the approach temperature and we have almost a 3C approach temperature advantage over the capacity sequenced plant.
This effect is even more favorable on a 1/3rd load day, where the wet bulb temperature is shown as 13C. Now lets consider the effect of this on the chiller.

## Slide 76
IPC
Speed control Demand based power relationships
(not set-point PID feedback loops)
Notes: An old fashion PID control loop was based on set points controlling 3 loops (chilled water loop, condenser water loop and refrigerant loop). Each loop used different set points and for example, the chilled water loop was controlled using DP reading across control valve, refrigerant loop was controlled by the chilled water leaving temperature while the cooling tower loop was controlled by the ambient temperature set point. This kind of control strategy posed difficulty in controlling multiple set points and matching these setting with constantly changing building demand for cooling.
As mentioned before, the chilled water plant rooms are being controlled the same way as they have been for the past 30-40 years, and this illustration explains one of the core issues around that missed opportunity.
Primarily, our chilled water plants are operated as three separate sub-systems, a PID feedback control loop for the CHW distribution system, and PID feedback control loop for the chiller, and a third PID feedback control loop for the condenser water. Each of these three “sub-systems” performs as efficiently as it can without consideration of how their operation effect the efficiency of the neighboring other two systems. The plant is definitely not an integrated system.
Lets now look at performance that is possible from an all variable speed plant with the IPC 11550 control system compared to today’s standard practice.

## Slide 77
Heat Energy Removed
Speed control Demand based power relationships
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
Notes: An old fashion PID control loop was based on set points controlling 3 loops (chilled water loop, condenser water loop and refrigerant loop). Each loop used different set points and for example, the chilled water loop was controlled using DP reading across control valve, refrigerant loop was controlled by the chilled water leaving temperature while the cooling tower loop was controlled by the ambient temperature set point. This kind of control strategy posed difficulty in controlling multiple set points and matching these setting with constantly changing building demand for cooling.
As mentioned before, the chilled water plant rooms are being controlled the same way as they have been for the past 30-40 years, and this illustration explains one of the core issues around that missed opportunity.
Primarily, our chilled water plants are operated as three separate sub-systems, a PID feedback control loop for the CHW distribution system, and PID feedback control loop for the chiller, and a third PID feedback control loop for the condenser water. Each of these three “sub-systems” performs as efficiently as it can without consideration of how their operation effect the efficiency of the neighboring other two systems. The plant is definitely not an integrated system.
Lets now look at performance that is possible from an all variable speed plant with the IPC 11550 control system compared to today’s standard practice.

## Slide 78
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
Heat Energy Removed
Power relationships optimized when 1kW of additional power to any device increases total cooling by same amount
Notes: An old fashion PID control loop was based on set points controlling 3 loops (chilled water loop, condenser water loop and refrigerant loop). Each loop used different set points and for example, the chilled water loop was controlled using DP reading across control valve, refrigerant loop was controlled by the chilled water leaving temperature while the cooling tower loop was controlled by the ambient temperature set point. This kind of control strategy posed difficulty in controlling multiple set points and matching these setting with constantly changing building demand for cooling.
As mentioned before, the chilled water plant rooms are being controlled the same way as they have been for the past 30-40 years, and this illustration explains one of the core issues around that missed opportunity.
Primarily, our chilled water plants are operated as three separate sub-systems, a PID feedback control loop for the CHW distribution system, and PID feedback control loop for the chiller, and a third PID feedback control loop for the condenser water. Each of these three “sub-systems” performs as efficiently as it can without consideration of how their operation effect the efficiency of the neighboring other two systems. The plant is definitely not an integrated system.
Lets now look at performance that is possible from an all variable speed plant with the IPC 11550 control system compared to today’s standard practice.

## Slide 79
At the Equal Marginal Performance Principle, the performance curves all have the same slope
Power relationships optimized when 1kW of additional power to any device increases total cooling by same amount
Notes: Demand Based Control, is the third patented control method to the Hartman LOOP. With demand based control we are essentially looking at the demand of the system and instructing the equipment where to operate. More specifically, given that we know the performance curves from manufacturers data, we can use technology to pre-determine the ideal power relationship between all four devices for each load scenario. With modern technology and IT network communication capabilities, we can manage the data, process the requirements, and communicate outward and inward to move the plant to the ideal set of power relationships.

## Slide 80
At the Equal Marginal Performance Principle, the performance curves all have the same slope
Power relationships optimized when 1kW of additional power to any device increases total cooling by same amount
Notes: Demand Based Control, is the third patented control method to the Hartman LOOP. With demand based control we are essentially looking at the demand of the system and instructing the equipment where to operate. More specifically, given that we know the performance curves from manufacturers data, we can use technology to pre-determine the ideal power relationship between all four devices for each load scenario. With modern technology and IT network communication capabilities, we can manage the data, process the requirements, and communicate outward and inward to move the plant to the ideal set of power relationships.

## Slide 81
Demand based power relationships adjust according to the chillers demand
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
Notes: An old fashion PID control loop was based on set points controlling 3 loops (chilled water loop, condenser water loop and refrigerant loop). Each loop used different set points and for example, the chilled water loop was controlled using DP reading across control valve, refrigerant loop was controlled by the chilled water leaving temperature while the cooling tower loop was controlled by the ambient temperature set point. This kind of control strategy posed difficulty in controlling multiple set points and matching these setting with constantly changing building demand for cooling.
As mentioned before, the chilled water plant rooms are being controlled the same way as they have been for the past 30-40 years, and this illustration explains one of the core issues around that missed opportunity.
Primarily, our chilled water plants are operated as three separate sub-systems, a PID feedback control loop for the CHW distribution system, and PID feedback control loop for the chiller, and a third PID feedback control loop for the condenser water. Each of these three “sub-systems” performs as efficiently as it can without consideration of how their operation effect the efficiency of the neighboring other two systems. The plant is definitely not an integrated system.
Lets now look at performance that is possible from an all variable speed plant with the IPC 11550 control system compared to today’s standard practice.

## Slide 82
CHWST set-point = 47°F
CHWST set-point = 45°F
Demand based power relationships adjust CHWST setpoint to the chillers demand
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
Notes: An old fashion PID control loop was based on set points controlling 3 loops (chilled water loop, condenser water loop and refrigerant loop). Each loop used different set points and for example, the chilled water loop was controlled using DP reading across control valve, refrigerant loop was controlled by the chilled water leaving temperature while the cooling tower loop was controlled by the ambient temperature set point. This kind of control strategy posed difficulty in controlling multiple set points and matching these setting with constantly changing building demand for cooling.
As mentioned before, the chilled water plant rooms are being controlled the same way as they have been for the past 30-40 years, and this illustration explains one of the core issues around that missed opportunity.
Primarily, our chilled water plants are operated as three separate sub-systems, a PID feedback control loop for the CHW distribution system, and PID feedback control loop for the chiller, and a third PID feedback control loop for the condenser water. Each of these three “sub-systems” performs as efficiently as it can without consideration of how their operation effect the efficiency of the neighboring other two systems. The plant is definitely not an integrated system.
Lets now look at performance that is possible from an all variable speed plant with the IPC 11550 control system compared to today’s standard practice.

## Slide 83
Chiller is sensitive to load changes and ambient wet-bulb temperature change
Tower pump speed and tower fan speed is adjusted to achieve the equal marginal performance principle
Load based CHWST set-point enables capacity trade off between the CHW supply pumps and the chiller.
A New Method Of Speed Control
Demand based power relationships adjust to the chillers demand
% Power
CHW Pumps
Chiller
CW Pumps
Tower Fans
Plant kW
CHWST set-point = 47°F
Notes: An old fashion PID control loop was based on set points controlling 3 loops (chilled water loop, condenser water loop and refrigerant loop). Each loop used different set points and for example, the chilled water loop was controlled using DP reading across control valve, refrigerant loop was controlled by the chilled water leaving temperature while the cooling tower loop was controlled by the ambient temperature set point. This kind of control strategy posed difficulty in controlling multiple set points and matching these setting with constantly changing building demand for cooling.
As mentioned before, the chilled water plant rooms are being controlled the same way as they have been for the past 30-40 years, and this illustration explains one of the core issues around that missed opportunity.
Primarily, our chilled water plants are operated as three separate sub-systems, a PID feedback control loop for the CHW distribution system, and PID feedback control loop for the chiller, and a third PID feedback control loop for the condenser water. Each of these three “sub-systems” performs as efficiently as it can without consideration of how their operation effect the efficiency of the neighboring other two systems. The plant is definitely not an integrated system.
Lets now look at performance that is possible from an all variable speed plant with the IPC 11550 control system compared to today’s standard practice.

## Slide 84
Design Envelope Integrated Plant Control
Patented Control Technology
Capacity based sequencing
Natural curve sequencing
Automation element
Parallel equipment staging (up/down)
Equipment speed control
Reset
PID feedback control loops
Ambient reset
Equal marginal performance principle
Demand based control
Traditional
Design Envelope demand based

## Slide 85
Armstrong Solutions: two configurations
Design Envelope
Integrated Plant Control IPC 11550
Notes: Armstrong offers 2 configurations within this family of plant automation solutions
We offer a plant level solution, the IPC 11550, and a building automation level solution, the OPTI-VISOR
The IPC is a full plant automation solution that communications directly with the mechanical gear and instrumentation, and takes responsibility for the control instructions to the devices.
The OPTI-VISOR control panel is an “advisor” to the existing building management system on how to optimally run the plant, best fan speed, best pump speed, etc. The BAS remains responsible for the automation of the plant equipment and receiving data from instrumentation
Both work on the all variable speed plant configuration and provide impressive paybacks on new project and retrofits

## Slide 86
Armstrong Design Envelope Integrated Plant Control – 2nd Configuration
OPTI-VISORTM

## Slide 87
Full plant automation
Remote Access
BMS Read/Write
Email alarms
Equipment Data
User Friendly Interface
10 Year Data Capacity
Factory Built & Tested
Design Envelope
Integrated Plant Control system
Notes: The default screen, or screen saver is a performance screen for the complete plant, and each of the main pieces of equipment in the plant.
This screen serves as a terrific training tool for the operator to observe the efficiency gains made by operating the plant in auto mode. If the operator feels that he can do better, the operator can observe how big the efficiency gain is in auto mode compared to manual mode.
The IPC 11550 ushers in a new era of user friendliness with a number of firsts.
Like many other system schematic displays, the IPC has icon driven control that enables the user to simply touch the symbol on the screen and bring up a status display. From the status display for that equipment, in this case we are showing a VIL pump, the operator can gather operating data and limits for that device. IN addition, the operator can change the operating status of that equipment, for example it can be electronically locked our of the duty status rotation by selection the HOA control to the “off” position. The device can be set to duty status 1,2,3 …, or as the standby piece of equipment. The equipment may also be set to a fixed speed, such as 65% FS.
More interestingly, the IPC equipment screen has two additional screen buttons titled “nameplate data” and I&O manual. The name plate button will bring up all the name plate data on the screen, saving the operator from having to go down to the plant with a pen and pad to get the information. The I&O button brings up the operating manual in PDF format. All of these functions are 100% available through the security encrypted web access license seats, 4 seats provided with each controller. This enable the operator of multiple facilities the ability to receive a warning by email from our controller, log in and take the suspect equipment out of service to prevent catastrophic failure, and then look up the necessary service parts in the manual to have them ordered for the next day. With more and more facilities have a single operator, this technology enables them to be in two places at once.

## Slide 88
Sequences for:
Design Envelope
Integrated Plant Control system
Emergency power transfer switch
All variable flow (VPF & VPVS)
Water side economizers
Thermal energy storage
Ground source (geothermal)
Dry air coolers (evaporative mist)
Compressor sequencing (large 11 kV dual compressor CS)
Demand limiting for demand response
Notes: We have developed a new series of control and product solutions that revolve around integrated control, one family of these is our line of all variable speed chilled water plant controls
They offer up to 60% energy savings per year on the whole chiller plant, through the factory integration of a new control algorithm.
These are robust factory built automation systems specific for a variety of chiller plant configurations, include all-variable speed plants: chillers, tower fans, CW pumps, and chilled water pumps.
These are site configurable devices, during commissioning the installer is inputting process data such as number of chillers and capacity of chillers, as opposed to creating any site specific operating code.
Important for your business is that they network with building automation systems, and enable remote access for your support of the customer relationship.

## Slide 89
At a glance display
Intuitive interface
System performance (operating status, setpoints, hardware data, etc.)
Trending
Data logs
Alarms
Setup and troubleshooting
Remote monitoring
Integrated Plant Controller – IPC11550 HMI
Notes: The default screen, or screen saver is a performance screen for the complete plant, and each of the main pieces of equipment in the plant.
This screen serves as a terrific training tool for the operator to observe the efficiency gains made by operating the plant in auto mode. If the operator feels that he can do better, the operator can observe how big the efficiency gain is in auto mode compared to manual mode.
The IPC 11550 ushers in a new era of user friendliness with a number of firsts.
Like many other system schematic displays, the IPC has icon driven control that enables the user to simply touch the symbol on the screen and bring up a status display. From the status display for that equipment, in this case we are showing a VIL pump, the operator can gather operating data and limits for that device. IN addition, the operator can change the operating status of that equipment, for example it can be electronically locked our of the duty status rotation by selection the HOA control to the “off” position. The device can be set to duty status 1,2,3 …, or as the standby piece of equipment. The equipment may also be set to a fixed speed, such as 65% FS.
More interestingly, the IPC equipment screen has two additional screen buttons titled “nameplate data” and I&O manual. The name plate button will bring up all the name plate data on the screen, saving the operator from having to go down to the plant with a pen and pad to get the information. The I&O button brings up the operating manual in PDF format. All of these functions are 100% available through the security encrypted web access license seats, 4 seats provided with each controller. This enable the operator of multiple facilities the ability to receive a warning by email from our controller, log in and take the suspect equipment out of service to prevent catastrophic failure, and then look up the necessary service parts in the manual to have them ordered for the next day. With more and more facilities have a single operator, this technology enables them to be in two places at once.

## Slide 90
IPC 11550 System – Typical Chilled Water Plant Performance Screen shot
Quick learning tool for operator to see impact of manual operation
Integrated Plant Controller – IPC11550

## Slide 91
Best in Class User Interface
Typical CHW Screen shot
Icon driven functionality
Icon contains operating status, set-points, and hardware data (nameplate information)
Integrated Plant Controller – IPC11550
Notes: The IPC 11550 ushers in a new era of user friendliness with a number of firsts.
Like many other system schematic displays, the IPC has icon driven control that enables the user to simply touch the symbol on the screen and bring up a status display. From the status display for that equipment, in this case we are showing a VIL pump, the operator can gather operating data and limits for that device. In addition, the operator can change the operating status of that equipment, for example it can be electronically locked our of the duty status rotation by selection the HOA control to the “off” position. The device can be set to duty status 1,2,3 …, or as the standby piece of equipment. The equipment may also be set to a fixed speed, such as 65% FS.
More interestingly, the IPC equipment screen has two additional screen buttons titled “nameplate data” and I&O manual. The name plate button will bring up all the name plate data on the screen, saving the operator from having to go down to the plant with a pen and pad to get the information. The I&O button brings up the operating manual in PDF format. All of these functions are 100% available through the security encrypted web access license seats, 4 seats provided with each controller. This enables the operator of multiple facilities the ability to receive a warning by email from our controller, log in and take the suspect equipment out of service to prevent catastrophic failure, and then look up the necessary service parts in the manual to have them ordered for the next day. With more and more facilities having a single operator, this technology enables them to be in two places at once.

## Slide 92
Full equipment performance trending
Automatic e-mail release on; alarms, warnings, or any user defined sequence
Optional plant monitoring and efficiency analysis by Armstrong
Available for a variety of system configurations and plant sizes
Integrated Plant Controller – IPC11550
Notes: Each system comes with 20 standard trends, and a simple one button “data log” function that downloads all data by email in excel format. Automatic emails are released on high and low level warnings.
When an alarm is received the operator can go to the alarm screen and touch the recent alarm description to receive a list of possible causes of the alarm to aid him in taking corrective action in what might be a highly stressed emotional state.

## Slide 93
Quarterly Reports (1st year)
Performance review
  Plant efficiency
  Equipment behaviour
  Plant maintenance
  Calibration to “worked-in” equipment
Design Envelope IPC 11550 Integrated Plant Controller
Notes: In today’s ever changing environment, there is a need for controls that are flexible, can respond quickly to changes and can easily adapt to new building requirements.
The IPC 11550 system is chilled water plant control system like no other.
It is a standalone solution that can work in harmony with a building automation system and a chiller control system, or it can be installed on its own and offer the customer more benefits than the two other approaches.
What is really exciting about the IPC 11550 System is that it offers the chilled water plant designer the opportunity to implement an “all-variable” speed plant, with a standard “off-the shelf” product. As a product, the IPC 11550 offers all the benefits that come with a manufacturers solution, versus a project specific controller, such as: ease of replacement parts, ease of troubleshooting, ease of modification through field adjustable parameters, ease of service and wide spread warranty support, mass produced economies of scale, and a high degree of rigor in the testing and approving of the product design and its “robustness”.
The IPC 11550 couldn’t come at a better time. Our global community has an ever increasing priority towards the environment, energy savings, and an expectation from us, the design community, to include those responsibilities in our profession. The patented control algorithm in the IPC 11550 system, enables us to design all variable speed plants that will use 60% less energy, on an annual average basis, than the current standard design practice. This is for a complete water-cooled chiller plant, including the tower fans, condenser water pumps, the chiller, and the chilled water pumps.
The way we achieve this new method of control is through the leveraging of micro-processor technology and IT networks. High tech solutions are creeping more and more into our every day lives, in the way we listen to music, using an I-pod or MP3 file instead of spinning a vinyl album, there is a new car on the market that offers the capability to store over 3000 songs on the vehicles resident memory, imagine how many cassette’s or CDs you would need. More closer to our industry, (next slide)

## Slide 94
Site Services
  Coordination meeting & project manager
  Commissioning & training
  First cooling season tuning
  Project energy analysis (load / WBT)
Design Envelope IPC 11550 Integrated Plant Controller
Notes: In today’s ever changing environment, there is a need for controls that are flexible, can respond quickly to changes and can easily adapt to new building requirements.
The IPC 11550 system is chilled water plant control system like no other.
It is a standalone solution that can work in harmony with a building automation system and a chiller control system, or it can be installed on its own and offer the customer more benefits than the two other approaches.
What is really exciting about the IPC 11550 System is that it offers the chilled water plant designer the opportunity to implement an “all-variable” speed plant, with a standard “off-the shelf” product. As a product, the IPC 11550 offers all the benefits that come with a manufacturers solution, versus a project specific controller, such as: ease of replacement parts, ease of troubleshooting, ease of modification through field adjustable parameters, ease of service and wide spread warranty support, mass produced economies of scale, and a high degree of rigor in the testing and approving of the product design and its “robustness”.
The IPC 11550 couldn’t come at a better time. Our global community has an ever increasing priority towards the environment, energy savings, and an expectation from us, the design community, to include those responsibilities in our profession. The patented control algorithm in the IPC 11550 system, enables us to design all variable speed plants that will use 60% less energy, on an annual average basis, than the current standard design practice. This is for a complete water-cooled chiller plant, including the tower fans, condenser water pumps, the chiller, and the chilled water pumps.
The way we achieve this new method of control is through the leveraging of micro-processor technology and IT networks. High tech solutions are creeping more and more into our every day lives, in the way we listen to music, using an I-pod or MP3 file instead of spinning a vinyl album, there is a new car on the market that offers the capability to store over 3000 songs on the vehicles resident memory, imagine how many cassette’s or CDs you would need. More closer to our industry, (next slide)

## Slide 95
Armstrong Design Envelope Integrated Plant Control
OPTI-VISORTM

## Slide 96
BAS
OPTI-VISOR™
The Armstrong OPTI-VISOR™ is an automated control solution that interfaces seamlessly with the existing building automation system to provide the optimal operating settings for a chiller plant.

## Slide 97
Connected to the BAS/BMS through the BMS communication network
Learns about:
building conditions, building load, and plant conditions from the BMS
OPTI-VISOR™ architecture

## Slide 98
OPTI-VISOR determines the operating parameters for the plant according to Design Envelope Integrated Plant Control
OPTI-VISOR then sends the control signal to the BMS
OPTI-VISOR™ architecture

## Slide 99
Flow: Primary Chilled Water
Temperatures: CHW supply and return, Condenser Water S&R
Power (kW): Chillers, pumps, & tower fan
Equipment status (on off alarm); Chillers, pumps, towers (ON)
Speed; pumps and fans
Optional: By-pass valve, WBT, DBT
OPTI-VISOR™ data points from BMS
Only
5
Data-sets
Required
Simplicity!

## Slide 100
Dataset to the BAS …
Chilled water supply temperature set point
Quantity of chillers, and cooling towers to run
Tower fan speed
Condenser pump speed
Only
4
Data-sets
Sent Out
Simplicity!
Data points for control OPTI-VISOR™

## Slide 101: OPTI-VISOR™
What does the Building Automation System continue to do?
Implement the sequence of operations for a variable primary plant
Responsible to safely stage equipment and operate it within its constraints

## Slide 102
What changes are required to the BAS
The BAS must now pickup, process, and implement the recommendations from the OPTI-VISOR
New data points and logic are added within the BAS code
OPTI-VISOR™

## Slide 103
What changes are required to the Plant Hardware (from VPF)
A VFD installed on each condenser water pump
New power cable from the MCC to the condenser water pump VFD, and from VFD to the pump
A new serial communications connection to the condenser pump vfds
OPTI-VISOR™

## Slide 104
Primary interface remains as the customer’s BMS
Device user interface screen
A web-based or intra-net user access for performance and data screens
Ideal for retrofit on projects with existing VPF BMS sequences
OPTI-VISOR™ User interfaces = three options

## Slide 105
OPTI-VISORTM Chilled-Water Plants Comparison
Notes: Looking at typical levels of efficiency for various scenario
Chiller Plant with optivisor – better than .55 kW/ton or 6.39 COP
Typical Chiller plant 0-5 years old- are around 0.75 kW/ton or 4.69 COP
Plants 6-10 Years old 0.90 kW/ton or 3.90 COP
Older planst are conservatively 1.1 kW/ton or 3.20 COP

## Slide 106
SAVINGS
25–30%
OPTI-VISOR
Installed on Variable Primary Systems, upgrading to All-variable
Retrofit impact: Payback periods as short as 6 months
Notes: If the BAS is controlling a variable primary flow plant with variable speed chillers the OPTI-VISOR can be used to upgrade the plants performance with an all-variable speed configuration.
For other situations, a retrofit of the IPC plant automation system can be applied.
Typical energy savings for these two different ranges of scenarios are shown (reference IP retrofit brochure and OPTI-Visor flyer for details)
Important for every high performance system is an automated method to ensure the performance of the asset, we have seen that a 20% erosion in plant performance because of contamination in a tower or chiller can cost the owner $40,000 in extra energy costs that could have been avoided if identified and corrected on day 1.
Armstrong offers an automated plant health management service for this, called ECO*PULSE

## Slide 107
ECO*PULSETM
HVAC Health Management Service

## Slide 108: ECO*PULSETM HVAC Health Service Essentially …
A subscription based service providing;

## Slide 109: ECO*PULSETM HVAC Health Service Why customers are interested?
  Every hour of operation with a system abnormality will cost;
    Energy
    Carbon emissions
    LEED certification
  At most times the plant is part loaded and the weather rarely remains constant
    Millions of conditions
    Rapidly changing
    Process needs automation
Can an operator manually observe plant operation and detect minor performance issues?

## Slide 110: ECO*PULSETM Standard on Armstrong plant automation
IPC 11550
Included
OPTI-VISOR
Included
IPC 9521
Optional

## Slide 111: Plant Optimization: Market Expectations 2008 – 2015 Learnings
Clear energy analysis (multiple decision makers)
Strong project management
Pre-test, field test, start-up, commission, and re-tune
Strong site presence and project lead role
Demonstrate and confirm performance commitment from the energy analysis
Continued retraining of staff
Enable their ability to confirm performance

## Slide 112
At Rapid City Hospital
Integrated plant controls deliver:
On an annual basis 35% energy cost savings
Design Envelope
OPTI-VISOR™ | New Construction
Notes: A long list of savings that adds up to a LCC and a true value based offering.

## Slide 113
At Headquarters TN Integrated Plant Controls Deliver:
On an annual basis 33% energy cost savings
Design Envelope
IPC | New Construction
Notes: A long list of savings that adds up to a LCC and a true value based offering.

## Slide 114
At Data Center (6000 TR)
OPTI-VISOR delivers:
On an annual basis 28% energy cost savings
Design Envelope
OPTI-VISOR™ | Retrofit
Notes: A long list of savings that adds up to a LCC and a true value based offering.

## Slide 115
OPTI-VISOR activation impact
Design Envelope demand based control was applied
Chart: Chiller Plant kW vs. Efficiency
January 19, 2012 9:00 am
Start-up of algorithm
Chiller plant kW
Efficiency kW/ton
0.7
0.6
0.5
0.4
0.3
0.2
0.1
0.0
31%

## Slide 116: Post-Installation Total Load vs. PUE
Chart: Total Load vs. PUE
kW
7600
7500
7400
7300
7100
7000
6900
6800
6700
January 19, 2012 9:00 am
Start-up of algorithm
Notes: 116

## Slide 117
A Real Customer Example
Methodist Hospital – Plant Optimization
At Methodist Hospital, Dallas Texas (4000 TR)
IPC11550 delivers:
On an annual basis 40% energy cost savings
Notes: 117

## Slide 118
A Real Customer Example
Methodist Hospital – Plant Optimization
IPC11550
Intelligent Fluid Management (iFMS)
Updated Plant Towers
$2 million, $450 incremental
$350k saved / year
<2 year payback
Notes: 118

## Slide 119
A Real Customer Example
Frito Lay
IPC | Retrofit | Rosenburg, Texas
At Frito Lay IPC Delivers:
On an annual basis 55% energy cost savings
Confirmed by an Independent power utility
Notes: 119

## Slide 120: Optimization Project Processes
Identify Opportunities
Site Walk-throughs & Evaluations
Qualify Opportunities
Engage Owner / End User
Identify Value Proposition(s) &
Identify Solution(s)
Complete Design / Build Solutions
& Engineering
Baseline Project
Secure available rebate dollars
Guarantee Performance &
Propose Solution(s)

## Slide 121
Tower or Chiller Retrofits
Additional Capacity Requirements
Refrigerant Change Outs
Utility Rebates ($0.05/kW-hr)
> 3,000,000 ton hours (2000tons at 3000 hours)
The “no-brainer” situations to watch for
They bring you <1 year payback on plant upgrade
OR
Regular
6 – 24 month paybacks
Notes: 121

## Slide 122: Utility Rebate Opportunities
Established Relationships with local utility providers
Custom & Detailed Reports to secure rebate funds
Baseline Project to maximize rebate funds
  Have Secured the following rebate $’s:
    Duke Energy: > $220k
    Xcel Energy: > $100k
    Hawaii Energy: > $80k
    Baltimore Gas & Elect: > $80k

## Slide 123: LEED Assessment

## Slide 124: LEED points contribution towards
Notes: Compliance with ASHRAE 90.1 2013
- provides 70% savings when system flow is at 50% of design
  - As flow/load decreases, the controller reduces the pump speed and keeps one valve as open as possible.
6.5.4.2 Hydronic Variable Flow Systems. HV AC pumping systems having a total pump system
power exceeding lO HP that include control valves designed to modulate or step open and close as
a function of load shall be designed for variable fluid flow and shall be capable of reducing
pump flow rates to 50% or less of the design flow rate. Individual chilled-water pumps serving
variable-flow systems having motors exceeding 5 hp shall have controls and/or devices (such as
variable-speed control) that will result in pump motor demand of no more than 30% of design
wattage at 50% of design water flow. The controls or devices shall be controlled as a function of
desired flow or to maintain a minimum required differential pressure. Differential pressure shall be
measured at or near the most remote heat exchanger or the heat exchanger requiring the greatest
differential pressure. The differential pressure setpoint shall be no more than 110% of that required
to achieve design flow through the heat exchanger. Where differential pressure control is used to
comply with this section and DOC systems are used, the setpoint shall be reset downward based on
valve positions until one valve is nearly wide open.

## Slide 125: Achieving 189.1 through Design Envelope Integrated Plant Control
Notes: 125

## Slide 126: USGBC Approved Course For Plant Control, authored by Armstrong (refers to all-variable plant control benefits)

## Slide 127: Key Selling points For Controls 1. Assess the opportunity (scope, contractor, consultant, owner) 2. Get it specified (if control is by BMS you can not sell added value after, controls contractor will carry BMS costs) 3. On retrofit stress the simplicity of use and reliability of the automation to the user and the owner (useless if left in manual, comfort of occupants is the key benefit). 4. Where energy is a decision motivator, include the EA, base line study, and discuss performance commitments.

## Slide 129: Energy Savings Guarantee (for retrofit projects only) Design Envelope IPC11550 and OPTI-VISOR Controls
Included in the price, the customer has the option of accepting our $100,000 Energy Savings Guarantee