TYPICAL SPECIFICATION

Instantaneous Water Heater (IWH) Control Type ‘Enhanced’

Models Designated IWH-xxx-W-x2-xx

General

The enhanced controller supplied with the IWH super system includes features that enable more accurate temperature control, increased data collection, increased communication capabilities. The microprocessor-based controller allows for parallel operation of multiple IWH systems. The following specification details these features.

Super System Control Features

- Microprocessor based controller with 2-line (24 characters) LCD display

- Membrane keypad designed specifically for IWH, panel mounted

- Master-Slave controller logic for the sequencing of parallel IWH units

- Closed loop feedback control with feed-forward compensation

- Proportional, Integral & Feed-Forward (P, I, & F) parameters tuned to optimize responsiveness with varying demand points

- Domestic Hot Water (DHW) supply temperature control to within (5°F, regardless of variance in boiler supply temperature*

- Six (6) Thermocouples monitoring primary and secondary loop temperatures at all times, with output displayed at the LCD display:

a)	Boiler supply temperature	d)	DHW recirculation temperature

b)	Boiler return temperature	e)	Cold water supply temperature

c)   DHW supply temperature	f)	Mixed (cold/recirc.) temperature

- Valve position displayed

- Alarm annunciation of high and low temperatures as well as pump failure

- Night-time DHW supply and recirculation temperature setback

- Energy saving logic to shut off primary pump during periods of no demand (5 minutes or greater)

- Serial communication link provided to tie in to Building Automation System for all data readings and alarms

- Password protected security coded panel to block unauthorized users

* Boiler supply temperature must be greater than 180°F for proper operation.