PFX Plate & Frame Heat Exchangers

Typical Specifications

DESIGN

The unit shall be provided with a galvanized or stainless-steel OSHA splash shield.

The units shall be built in accordance with ASME code and when necessary be ASME Code stamped board registered.

The unit shall be built in accordance with NSF 61 when the unit is required for domestic water applications.

FRAME

The frame plate and pressure plate should be carbon steel SA 516 grade 70.

The frame and pressure plate shall be of sufficient thickness to meet the ASME design pressure. Stiffeners or support brackets are not allowed.

Carbon steel frame components shall be painted with Armstrong “Harvester Red” epoxy paint.

Units with four-inch or greater connections shall be unlined or alloy lined studded ports to mate with raised face or flat faced ANSI flanges. Rubber liners are not allowed.

Units with two-inch or smaller connections shall have carbon steel female tapped NPT or male NPT connections if an alloy material is required.

Units with two and half or three-inch connections shall be either studded ports or NPT as described above.

The frame design shall allow the thermal plates to be supported by the carry bar, top bar. The guide bar, bottom bar, shall only help properly align the plates.

A roller assembly from the carry bar shall support the pressure plate for units taller than 50".

Tightening bolts shall be zinc plated carbon steel SA193 B7.

PLATES

Plates shall be constructed of Stainless Steel (304 or 316 L) or Titanium.

Plates shall be pressed with a herringbone corrugation to optimize heat transfer.

Plates shall use an integral rolled edge hanging system to provide a rigid hanger device between the plate and carry bar and guide bar. Welded on hanging brackets or stiffeners are not acceptable.

Plates shall be permanently marked to indicate plate material and thickness.

Plates for all NSF 61 certified units designed for domestic water application are to be constructed of 316L Stainless Steel double wall pressed in a once-step stamping process.

GASKETS

The gaskets shall be a one-piece construction with a double gasket barrier at the port region. The area isolated by the double gasket shall be vented to the atmosphere, so that a gasket failure is detected by leakage to the exterior prior to any possible cross contamination.

Gaskets are to be “mechanically fixed”. Glued gaskets are not acceptable.

The gaskets are to be made of NBR or EPDM depending on application.

Gaskets for all NSF 61 certified units designed for domestic water application are to be made of NBR or EPDM with an FDA approved material.

SELECTION, CERTIFICATION AND TESTING

The manufacturer shall hydro-test the unit to 1.3 times the design pressure as directed by ASME Code.

The manufacturer shall provide NSF 61 unit when the unit is required for domestic water applications.

5.3. The plate and frame heat exchanger manufacturer must be a certified member of NSF 61 - Drinking Water System Components - Health Effects.

# Text boxes

File No: 113.16

Date:  December 19, 2023

Supersedes: 113.16

Date: October 14, 2015