4700 Vertical Multistage Pumps

File No: 47.103

Date: October 28, 2025

Supersedes: 47.10

Date: New

Typical Specifications

Construction

Supply and install, as shown on the plans and specifications, Armstrong 4700 Vertical Multistage (VMS) pump. The pump shall have a continuously rising curve from minimum head to shut off condition and shall have a motor installed that is suitable for the full range of the published performance curve.

- Models VMS-03, 05, 10, 15 & 20: All wetted surfaces shall be manufactured from Type 304 stainless steel.

- Models VMS-32, 45 & 64: All hydraulic components will be manufactured from Type 304 stainless steel with cast iron bottom casing.

Hydraulic Components & Mechanical Seal

The stainless steel shaft shall be made of either AISI304, 316 or 329A depending on the model number and shall be fitted with Tungsten Carbide shaft sleeve bearing. The mechanical seal shall be suitable for the full pressure and temperature range of the pump and shall be fitted with Silicon Carbide rotating face and Carbon stationary face. The cartridge mechanical seal design enables replacement without disassembling the motor bracket

Internal Components

The low axial thrust impeller design enables a longer motor bearing life. The liner ring is a self-aligning, floating design constructed to prevent swelling at high temperatures and deformation from pressure fluctuations.

External Components

Air vent in casing cover allows proper venting that prevents air entrapment and dry runs. Fill port in casing enables water filling for priming purposes. Coupling shall be protected by a guard that can be easily removed for inspection and maintenance.

Connections

The base mounted pump shall be assembled in a vertical shaft configuration with the suction and discharge connections being 180° in-line at the bottom.

Suction and discharge connections shall have same size flanges with an ANSI 150 (250 or 300, as appropriate) rating.

Motor

Supply a standard NEMA design, 'C face' 2-pole squirrel cage induction type motor with NEMA Prem (12.12) efficiency and TEFC enclosure.