System Envelope Fluid Management

File No: 91.204

Date: January 19, 2026

Supersedes: New

Date: New

Station - SEFMS

Typical Specifications

# GENERAL

## Description

Provide a factory-assembled, modular fluid management station consisting of pumps, integrated piping, isolation devices, controls, and power distribution, designed to deliver the required system flow and head across the defined operating range.

The system shall be engineered, tested, and validated as a complete assembly and shall operate within a defined performance envelope to ensure stable flow, efficient pump staging, and reliable operation under varying load conditions.

## Performance Requirements

The fluid management station shall be selected and validated to meet the following minimum requirements:

- Design flow: ______ GPM (L/s)

- Design head: ______ ft (m)

- Minimum system efficiency at design condition: ______ %

- Minimum flow turndown ratio: ______ :1

- Redundancy requirement: ______ %

Selection shall be based on performance mapping that validates system operation across the full expected range of flow, head, and staging conditions, not solely at a single duty point. The system shall be capable of maintaining stable operation across the full range of design flow, minimum turndown, and redundancy conditions without manual field tuning or control logic modification.

## System Function

The system shall:

Maintain stable hydraulic performance within the validated operating envelope

Provide efficiency-based pump staging without reliance on BAS sequencing

Prevent operation in unstable or non-validated operating regions

Provide real-time performance data for monitoring, analysis and verification

# SYSTEM CONSTRUCTION

## General Assembly

The station shall be factory-assembled on a rigid structural frame capable of supporting the fully flooded operating weight without detrimental deflection.

The assembly shall be suitable for lifting, rigging, and installation in accordance with manufacturer requirements.

## Hydraulic Components

Each pumping module shall include, as a minimum:

Suction-side isolation valve

Low-loss suction guide with flow-stabilizing vanes

Removable stainless-steel strainer with optional fine-mesh start-up strainer

Pressure gauges upstream and downstream of the pump

Drain connection(s)

Discharge isolation valve

Multi-module assemblies shall include factory-supplied interconnecting headers, supports, and mechanical couplings to allow on-site module assembly without welding.

## Modular Configurations

The system shall be available in:

Single-module configuration

Two-module configuration

Three-module configuration

Each configuration shall be governed by the same performance mapping methodology and envelope enforcement logic.

# CONTROLS & OPERATION

## Control Strategy

The system shall utilize integrated pump controls capable of:

Sensorless flow estimation with minimum ±5% accuracy

Parallel pump staging based on efficiency optimization

Independent operation from the BAS for staging and stability

Communication to the BAS via open protocols

Control strategies relying solely on fixed speed staging, time-based sequencing, or BAS-only logic shall not be acceptable.

## Operating Envelope Enforcement

The control system shall enforce operation within the validated performance envelope established during selection.

Operation outside validated flow, head, or power limits shall be restricted or alarmed to prevent unstable or inefficient operation.

## Data & Communication

The system shall provide real-time data including:

Flow

Head

Power

Operating status

Data shall be available locally and digitally transmitted via BACnet and/or Modbus protocols.

# ELECTRICAL

## Power Distribution

Each module shall include a factory-assembled power distribution panel with:

Single incoming power connection per module

Main disconnect

Branch protection for each motor

UL / cUL / CSA certification

Minimum NEMA Type 12 enclosure for indoor installations

## Wiring

All wiring shall be factory-installed, labeled, and tested. Field wiring shall be limited to incoming power, communications, and external instrumentation.

# QUALITY ASSURANCE & FACTORY TESTING

## Manufacturer Qualifications

The manufacturer of the packaged system shall:

Maintain an ISO 9001-certified quality management system

Be listed as a UL-approved manufacturer of packaged pumping systems

## Factory Testing

The complete system shall be factory tested as an assembled unit and shall include, at a minimum:

Hydrostatic pressure testing of all piping

Verification of control sequences and alarms

Functional testing of pump staging and rotation

Validation of operation within the defined performance envelope

Test documentation shall be available upon request.

# SUBMITTALS

Submit the following for review:

Performance mapping documentation demonstrating validated operating envelope

General arrangement drawings

Piping and instrumentation diagrams

Electrical schematics

Control sequence of operation

Installation, operation, and maintenance manuals

# INSTALLATION

Installation shall be performed in accordance with manufacturer instructions. For multi-module systems, on-site assembly shall be limited to mechanical coupling of factory-supplied modules.

No field welding or internal wiring (except between modules) shall be required.

# ACCEPTABLE MANUFACTURERS

Factory-assembled fluid management stations meeting the requirements of this specification shall be provided by one of the following:

Armstrong Fluid Technology – System Envelope Fluid Management Station (SE-FMS)

Approved equal

Substitutions

Substitutions shall only be considered if the proposed system demonstrates:

Equivalent performance mapping methodology

Enforced operating envelope validation

Factory-tested integrated assembly

Sensorless parallel staging capability

Equivalent digital performance verification