TYPICAL SPECIFICATION

Horizontal Fire Pump - Electric Motor Driven*

Supply and install as indicated on plans one (1) fire pump system consisting of:

1. PUMP

One Armstrong Darling , SERIES 4600F, Size _____________ double suction horizontal split case fire pump listed by Underwriters Laboratories of Canada (ULC), Underwriters Laboratories Inc. (UL) and approved by Factory Mutual FM) having a capacity of _______________ USGPM for a pressure boost of _______________ PSIG. Suction pressure ______________ PSIG.

Pump casing shall be of cast iron, axially split with a 15° angle that will minimize NPSH requirements and dimensions. Lower half shall contain suction and discharge nozzles. Suction and discharge connections shall be on the same elevation. Top half and rotating element shall be removable without disturbing the piping. Casing shall be fitted with replaceable bronze wearing rings. Impeller shall be bronze, double suction, enclosed type fully balanced and keyed to an alloy steel shaft. Shaft shall to be fitted with replaceable bronze sleeves. Shaft shall be mounted in two dust tight deep grooves, sealed, and permanently greased ball bearings.

Bearings shall be mounted in cartridge type housing so that they shall be replaceable without opening pump casing. Bearings shall be easily removable by rotating bearing removal nut. No special tools or bearing puller are to be necessary.

Each stuffing box shall be fitted with a three piece bronze gland. Stuffing box shall be fitted with a stuffing box extension to facilitate the packing rings removal. Packing rings shall be removable without disturbing wetted parts or the pump bearings. Water seal rings made from non-corroding material shall be piped to pump volute.

2. ELECTRIC MOTOR

The fire pump shall be directly coupled through flexible coupling to a horizontal electric motor with a maximum HP of_____________ at __________RPM, _________ VOLT, _______ PHASE _________ CYCLE. Motor shall be open drip proof, standard efficiency with 1.15 service factors.

3. MINIMUM FITTINGS

The pump shall be supplied with the following accessories:

• One (1) combination suction gauge 3-1/2” dial type with 1/4” cock and lever handle.

• One (1) discharge gauge, 3-1/2” dial type, with 1/4” cock and lever handle.

• One (1) air release valve.

• One (1) casing pressure relief valve.

4. OTHER ACCESSORIES

Pump shall be fitted with one (1) eccentric suction reducer and one (1) concentric discharge increaser (by mechanical contractor) to fit NFPA20 recommended piping sizes.

One (1) outside test header shall be supplied with one (1) set of ____ x 2 1/2” hose valves with caps and chains.

5. FIRE PUMP CONTROLLER

The fire pump controller shall be specifically approved for fire pump service by ULC, UL or FM. The controller shall be of the combined manual and automatic stop, __________________________starting method, Model _____________

as manufactured by______________. All equipment shall be enclosed in approved drip proof enclosure. The control equipment shall be completely assembled, wired and tested at point of manufacture prior to shipment.

Circuit breaker shall have an interrupting capacity of _________kAmps or a withstand rating of ____________ kAmps RMS.

Water pressure switch shall be suitable for _________ PSI working pressure.

5 A. FIRE PUMP CONTROLLERS AND AUTOMATIC TRANSFER SWITCH COMBINATION

The automatic transfer switch controller combination shall be approved by UL, ULC or FM, Model ________________. The automatic transfer switch and the pump controller shall each be mounted in separate enclosure, mechanically attached to form one unit and provide for protected interlock wiring.

The automatic transfer switch shall be capable of automatic power transfer from normal to alternate_______________ (generator / second utility) emergency power source in case of normal supply failure and automatically re-transfer after restoration of normal power conditions.

6. JOCKEY PUMP

The jockey pump shall be manufactured by_____________ Model No.______________ for a capacity of __________ USGPM and a pressure boost of ____________ PSIG. The jockey pump shall be driven by an open drip proof electric motor of_______HP ________ RPM __________ VOLT ______ PHASE________ CYCLE.

7. JOCKEY PUMP CONTROLLER

The jockey pump shall be controlled by an automatic jockey pump controller model ___________ with full voltage starter.

8. MOUNTING AND TESTING

The pump shall be suitable for a maximum working pressure of __________. Pump shall be hydrostatically tested at twice the maximum working pressure for at least 5 minutes. The pump shall be performance tested at rated speed. The pump shall furnish not less than 150% of rated capacity at a pressure not less than 65% of rated head. The shut-off total head of the pump should not exceed 140% of total rated head. A certified test curve, indicating the flow, head, power and efficiency shall be supplied. The fire pump and electric motor shall be base mounted and aligned at the pump manufacturer’s factory. Final alignment shall be made after installation on site. Please refer to Armstrong Fire Pump Catalogue for Diesel Driven Typical Specifications.