TYPICAL SPECIFICATION

Flo-Trex Valves

Furnish and install on the discharge side of each pump an Armstrong Model FTV Flo-Trex Combination Valve.  Each

valve is to incorporate the following three functions in one body:

- Tight shut-off

- Spring-closure type silent non-slam check

- Effective throttling design capability

Note:  The throttling function should not be used in variable speed applications and is to be used only to alleviate any noise, vibration or cavitation where a speed reduction to design flow solution will not eliminate these symptoms

The body shall have (2) 1/4” NPT connections on each side of the valve seat. One connection on each size shall have brass pressure and temperature metering ports, with Nordel check valves and gasketed caps. The other connection on each side shall be supplied with brass drain plugs. Metering ports are to be interchangeable with drain plugs to allow for measurement flexibility when installed in tight locations. The valve disk shall be bronze plug & disc type with high impact engineered resin seat to ensure tight shut-off and silent check operation.

The valve stem shall be stainless steel with flat surfaces provided for adjustment with open-end wrench.

For Grooved Piping: The valve body shall be ductile iron with grooved ends and Armstrong anti-rotation Armgrip® lugs on the inlet and outlet of the body.

Flange adapters (Where necessary) are to be Armstrong Armgrip® ANSI 125 (ANSI 250, PN16,  PN25) ductile iron flanges with anti-rotation lugs and EPT gaskets.

For ANSI 150 (PN16) Welded Flanged Piping:  The valve body shall be Cast Iron with ANSI 125 (PN16) flanged ports.

For ANSI 300 Welded Flanged Piping:  The valve body shall be Ductile Iron with ANSI 250 (PN25) flanged ports.

The valve shall be selected and installed in accordance with the manufacturer’s instructions and be suitable for the pressure and temperature specified.

Insulation (Available 2.5” – 6” Flo-Trex Valves)

Each valve shall be furnished with a pre-formed removable PVC insulation jacket to meet ASTM D1784 Class 14253-

C, MEA #7-87, ASTM-E-84 and ASTM136 with a flame spread rating of 25 or less and a smoke development rating

of 50 or less. There will be provided sufficient mineral fiberglass insulation to meet ASHRAE 90.1-1989 specifications in operating conditions with maximum Fluid Design Operating Temperature Range of 141°F-200°F (60°C-93°C) and Mean Rating Temperature of 125°F (52°C).